## Slide 1: Debre Markos University Debre Markos Institute of Technology
School of Electrical and computer Engineering
Introduction to Power system
2. Basic Concepts in Electric Power system

## Slide 2
Power in single phase a.c. system
The instantaneous power in watts absorbed by an electrical load is the product of the instantaneous voltage across the load in volts and the instantaneous current into the load in amperes
Assuming the load voltage is
Purely resistive load
For a purely resistive load, the current into the load is in phase with the load voltage, , and the current into the resistive load is

## Slide 3
The instantaneous power absorbed by the resistor is
The instantaneous power absorbed by the resistor has an average value

## Slide 4
Purely inductive loads
For a purely inductive load, the current lags the voltage by 90 degree,
is the inductive reactance
The instantaneous power absorbed by the inductor is
The instantaneous power absorbed by the inductor is a double-frequency sinusoid with zero average value

## Slide 5
General RLC Load
For a general load composed of RLC elements under sinusoidal-steady-state excitation, the load current is of the form
The instantaneous power absorbed by the load is then

## Slide 6
the instantaneous power absorbed by the load has two components:
  One can be associated with the power (t) absorbed by the resistive component of the load (Real power), and
  the other can be associated with the power (t) absorbed by the reactive (inductive or capacitive) component of the load (Reactive Power).

## Slide 7: Complex Power
The Active power is the power that is dissipated in the resistance of the load.
It uses the same formula used for DC (V & I are the magnitudes, not the phasors):
The reactive power is the power that is exchanged between reactive components (inductors and capacitors)
The formulas look similar to those used by the active power, but use reactance instead of resistances.

## Slide 8
For circuits operating in sinusoidal-steady-state, real and reactive power are conveniently calculated from complex power, defined below.
Let the voltage across a circuit element be , and the current into the element be . Then the complex power S is the product of the voltage and the conjugate of the current:
is the angle b/n the voltage and current
So S is recognized as
      P = real power
      Q= reactive power and
      Power factor

## Slide 9
The magnitude of the complex power S is called the apparent power, it signifies the rating of equipments (generators, Transformers, etc)

## Slide 10
Power Triangle
From these complex power expressions, the following can be stated:
  A resistor absorbs (positive) real power, W, and zero reactive power, var.
  An inductor absorbs zero real power, W, and positive reactive power, var.
  A capacitor absorbs zero real power, W, and negative reactive power, var.
  Alternatively, a capacitor delivers positive reactive power, .

## Slide 11: Direction of Power Flow
Consider the current and voltage of figure (a) where a dc current I is flowing through a battery.
If the voltmeter and ammeter both read upscale to show E=100 V and I=10 A, the battery is being charged (absorbing energy) at the rate given by the product EI= 1000 W.
On the other hand , if the ammeter connections have to be reversed in order that it reads upscale with the current arrow still in the direction shown , then I =-10 A and the product EI = -1000 W, the battery is discharging (delivering energy)

## Slide 12
The same considerations applied to the ac circuit relationships.
Figure (b) shows an ac system with an ideal voltage source with polarity marks to indicate the terminals which is positive during the half cycle of instantaneous voltage.
Similarly the arrow indicates the direction of current I into the box during the positive half cycle of the current.
By definition the power absorbed inside the box is
Where 𝛉 is the phase by which I lags V.
If P = is positive real power is absorbed by E.
If P = is negative real power is supplied by E.

## Slide 13
Generally , we can determine the P and Q absorbed or supplied by any ckt as enclosed in a box with entering current I and voltage V having polarity as shown in the figure given below.
If Pcircuit absorbs real power
If P circuit supplies real power
If Q, circuit absorbs reactive power (I lags V)
If Q, circuit supplies reactive power (I leads V)

## Slide 14: Balanced three phase system
Three sources connected to 3 loads using four-wire system
Sources have EQUAL frequency but DIFFFERENT phases
+

+

+

Van
Vbn
Vcn
a
n
b
c
Balanced three phase voltages:
  same magnitude (VM )
  120 phase shift

## Slide 15
Balanced three phase currents:
  same magnitude (IM )
  120 phase shift

## Slide 16
Positive (abc) Sequence
Negative (acb) Sequence

## Slide 17
The solution of a three phase network under balanced conditions is easily carried out by solving the single phase network corresponding to the reference phase.
Figure 2.1 shows a simple, balanced three phase network
The generator and load neutrals are therefore at the same potential, so that
Figure 2.1

## Slide 18
The neutral impedance does not affect network behavior
For the reference phase a
The current and the voltage in the other phases have the same magnitude but progressively shifted by
Equation 2.1 corresponds to the single phase network of figure 2.2 below
The solution of fig. 2.2 completely determines the solution of the three phase network
Figure 2.2

## Slide 19
Consider the case where a three phase transformer forms part of a three phase power system
If the transformer is Y/Y connected as shown in fig. 2.3a, in the single phase equivalent of the three phase circuit it can be obviously represented by a single phase transformer (as in fig. 2.3b) with primary and secondary pertaining to phase a of the three phase transformer
Figure 2.3

## Slide 20
If the transformer is Y/∆ connected as in figure 2.4a below, the delta side has to be replaced by an equivalent star connection as shown doted so as to obtain the single phase equivalent of fig. 2.4b
When the load is balanced, the impedance of each leg of the Y is one third the impedance of each leg of the ∆
The circuit is modeled by the single phase equivalent circuit
Since both phase voltage and line current shift through the same phase angle from star to delta side, the transformer per phase impedance and power flow are preserved in the single phase equivalent.

## Slide 21
Figure 2.4
It may be noted here that irrespective of the type of connection, the transformation ratio of the single phase equivalent of a three phase transformer is the same as the line-to-line transformation ratio

## Slide 22
Delta-Wye Transformation
To simplify analysis of balanced systems:
  ∆- connected loads can be replaced by
    Y – connected loads with
  ∆ - connected sources can be replaced by
    Y – connected sources with

## Slide 23: Power in balanced three phase system
If the magnitude of the voltages to neutral for a Y-connected load is
𝗅𝗅=𝗅𝗅=𝗅𝗅=𝗅𝗅 and if the magnitude of the phase current for a Y-connected load is
𝗅𝗅=𝗅𝗅=𝗅𝗅=𝗅𝗅 then, the total three phase power and the total three phase var is,
P=3 𝗅𝗅 Q=3 𝗅𝗅
Where is the angle by which phase current lags the phase voltage.
If the magnitudes of line-to-line voltage and line current are 𝗅𝗅 and 𝗅𝗅, respectively,
P= 𝗅𝗅 Q= 𝗅𝗅
The total volt-amperes of the load is
𝗅𝗅

## Slide 24
Reading Assignment
Unbalanced three phase system
Voltage and current in unbalanced three phase system
Power in unbalanced three phase system
Read for the above topics and submit the report individually until 04/08/2011 E.C.

## Slide 25
PER-UNIT REPRESENTATION
Computations for a power system having two or more voltage levels become very cumbersome when it is necessary to convert currents to a different voltage level wherever they flow through a transformer (the change in current being inversely proportional to the transformer turns ratio).
In an alternative and simpler system, a set of base values, or base quantities, is assumed for each voltage class, and each parameter is expressed as a decimal fraction of its respective base.
For instance, suppose a base voltage of 345 kv has been chosen, and under certain operating conditions the actual system voltage is 334 kV: then the ratio of actual to base voltage is 0.97.
The actual voltage may then be expressed as 0.97 per-unit. In an equally common practice, per-unit quantities are multiplied by 100 to obtain percent quantities: our example voltage would then be expressed as 97 percent.
Per-unit and percent quantities and their bases exhibit the same relationships and obey the same laws (such as Ohm's law and Kirchhoff’s laws) as do quantities in other systems of units.

## Slide 26
A minimum of four base quantities is required to completely define a per-unit system: these are voltage, current, power, and impedance (or admittance). If two of them are set arbitrarily, then the other two become fixed.
Base values can be determined by three ways
  Taking the largest value
  Taking the total sum
  Any arbitrary
The per unit value of any quantity is the ratio of the actual value in any units to the chosen base quantity of the same dimensions expressed as a decimal.
In power systems the basic quantities of importance are voltage, current, impedance and power. For all per unit calculations a base KVA or MVA and a base KV are to be chosen.
Once the base values or reference values are chosen, the other quantities can be obtained as follows:

## Slide 27
Where base KVA and base KV are the total or three phase values.
If phase values are used
Base current in amperes =
Base impedance in ohm =
Base Impedance in ohm =
In all the above relations the power factor is assumed unity, so that
Base power K W = base K VA
Now, Per unit impedance=

## Slide 28
Selecting the total or 3-phase KVA as base KVA, for a 3-phase system
Base current in amperes =
Base Impedance In ohms =
Base Impedance in ohms =
Now, Per unit impedance =

## Slide 29
Some times, it may be required to use the relation
actual Impedance in ohm =
Very often the values are in different base values. In order to convert the per unit impedance from given base to another base, the following relation can be derived easily.
Per unit impedance on new base

## Slide 30
In general :
Base current = base volt amperes/base voltage (in amperes)
Base impedance = base voltage/ base current (in ohms)
Per-unit voltage = actual voltage / base voltage (per unit, or pu)
Per-unit current = actual current / base current (per unit, or pu)
Per-unit impedance = actual impedance /base impedance (per unit. or pu)
The impedances of transmission lines are expressed in ohms, but can be easily converted to pu values on a given voltampere base using above expressions.

## Slide 31
Advantages of Per Unit System
1. While performing calculations, referring quantities from one side of the transformer to the other side serious errors may be committed. This can be avoided by using per unit system.
2. The p.u systems are ideal for the computerized analysis and simulation of complex power system problems.
3. Voltages, currents and impedances expressed in per unit do not change when they are referred from one side of transformer to the other side. This is a great advantage'.
4. Per unit impedances of electrical equipment of similar type usually lie within a narrow range, when the equipment ratings are used as base values.
5. Transformer connections do not affect the per unit values.
6. Manufacturers usually specify the impedances of machines and transformers in per unit or percent of name plate ratings.

## Slide 32: Example
Solve for the current, load voltage and load power in the circuit shown below using per unit analysis with an SB of 100 MVA, and voltage bases of 8 kV, 80 kV and 16 kV.
Original Circuit

## Slide 33
Same circuit, with
values expressed
in per unit.

## Slide 35
To convert back to actual values just multiply the per unit values by their per unit base