## Slide 1: Debre Markos University Debre Markos Institute of Technology
School of Electrical and computer Engineering
Introduction to Power system
5. Current and Voltage Relations on a Transmission Line

## Slide 2
INTRODUCTION
This chapter deals with the representation and performance of transmission lines under normal operating conditions.
Transmission lines are represented by an equivalent model with appropriate circuit parameters on a per-phase basis.
The terminal voltages are expressed from one line to neutral, the current for one phase and, thus, the three-phase system is reduced to an equivalent single phase system.
This model used to calculate voltages, currents, and power flows depends on the length of the line.

## Slide 3
ABCD Constants
It is convenient to represent a transmission line by the two port network, where in the sending-end voltage Vs and current Is are related to the receiving-end voltage VR and IR through A, B, C and D parameters (ABCD constants) as
Figure: Two-port representation of Tx lines
A, B, C and D are the parameters that depend on the transmission line constants R, L, C and G

## Slide 4
The ABCD parameters are, in general complex numbers
  A and D are dimensionless
  B has units of Ohms and
  C has units of Siemens
Also the following identity holds for ABCD constants

## Slide 5
SHORT TRANSMISSION LINES
Capacitors may be ignored without much error if the lines are less than 80 km long or if the voltage is not over 66 kV
The short line model is obtained by multiplying the series impedance per unit length by line length
The short line model on per-phase basis is shown in figure 5.2 below
Figure 5.2 Short line model

## Slide 6
If a three phase load with apparent power is connected at the end of the transmission line, the receiving end current is obtained by:
The relationship between sending-end, receiving-end voltages and currents can be written as in the form of equation 5.1

## Slide 7
The phasor diagram for the short line is shown in figure 5.3
Figure 5.3 Phasor diagram for short transmission line
Voltage Regulation and Efficiency
Voltage regulation of the transmission line may be defined as the percentage change in voltage at the receiving end of the line ( expressed as percent of full load voltage) in going from no-load to full-load

## Slide 8
For a short line, ( ) and
Voltage regulation is a measure of line voltage drop and depends on the load power factor
Voltage regulation will be poorer at low lagging power factor loads. With capacitive loads (leading P.f.) regulation may become negative

## Slide 9
Once the sending end voltage is calculated the sending end power is obtained by

## Slide 10
  Example
  A 220 kV, three phase transmission line is 40 km long. The resistance per phase is 0.15 Ω per km and the inductance per phase is 1.3263 mH per km. The shunt capacitance is negligible. Use the short line model to find the voltage and power at the sending end and the voltage regulation and efficiency when the line is supplying a three phase load of
  a). 381 MVA at 0.8 power factor lagging at 220 kV
  b). 381 MVA at 0.8 power factor leading at 220 kV
  Solution
  (a). The series impedance per phase is

## Slide 14
MEDIUM TRANSMISSION LINE
For the lines more than 80 km long and below 250 km in length are treated as medium lines, and the line charging current becomes appreciable and the shunt capacitance must be considered.
The capacitance is uniformly distributed over the entire length of the line. However, in order to make the calculations simple, the line capacitance is assumed to be lumped or concentrated in the form of capacitors shunted across the line at one or more points. Such a treatment of localizing the line capacitance gives reasonably accurate results.
The most commonly used methods (known as localized capacitance methods) for the solution of medium transmissions lines are :
(i) End condenser method (ii)Nominal T- method (iii) Nominal π - method.
Figure 5.4 nominal π model for medium length line

## Slide 15
The sending end voltage and current for the nominal π model are obtained as follows:
From KCL the current in the series impedance designated by is

## Slide 17
Example 1
Determine the efficiency and regulation of a 3-phase, 150 km long, 50 Hz transmission line delivering 20 MW at a power factor of 0.8 lagging and 66 kV to a balanced load. Resistance of the line is 0.075 Ω/km, inductance of the line and capacitance per phase is 1.117 mH/km and 9.933 nF/km respectively. Use nominal π method.
Solution

## Slide 21
Example 2
Determine the voltage, current and power factor at the sending end of a 3 phase, 50 HZ, overhead transmission line 160 km long delivering a load of 100 MVA at 0.8 pf lagging and 132 kV to a balanced load. Resistance per km is 0.16 Ω, inductance per km is 1.2 mH and capacitance per km per conductor is 0.0082 . Use nominal π method.
Solution

## Slide 24
LONG TRANSMISSION LINE
For the short and medium length lines reasonably accurate model were obtained by assuming the line parameters to be lumped.
In case the lines are more than 250 km long, for accurate solutions the parameters must be taken as distributed uniformly along the length as a result of which the voltage and currents will vary from point to point on the line.
In this section, expressions for voltage and current at any point on the line are derived. Then, based on these equations, an equivalent π model is obtained for long transmission line.
Figure 5.6 shows one phase of a distributed line of length km, the series impedance per unit length is shown by the lowercase letter z, and the shunt admittance per phase is shown by the lowercase letter y, where

## Slide 25
  Figure 5.5: Long line with distributed parameters
  Consider a small segment of line ∆x at a distance x from the receiving end of the line
  From Kirchhoff's voltage law

## Slide 27
Propagation constant measures the change undergone by the source quantity as it propagates from one port to the next
Attenuation constant measures the attenuation of an electromagnetic wave propagating through a medium per unit distance from the source

## Slide 32: Ferranti Effect
A long transmission line draws a substantial quantity of charging current. If such a line is open circuited or very lightly loaded at the receiving end, receiving end voltage being greater than sending end voltage in a transmission line, is known as Ferranti effect.
All electrical loads are inductive in nature and hence they consume lot of reactive power from the transmission lines.
Hence there is voltage drop in the lines. Capacitors which supply reactive power are connected parallel to the transmission lines at the receiving end so as to compensate the reactive power consumed by the inductive loads.

## Slide 33
As the inductive load increases more of the capacitors are connected parallel via electronic switching. Thus reactive power consumed by inductive loads is supplied by the capacitors thereby reducing the consumption of reactive power from transmission line.
However when the inductive loads are switched off the capacitors may still be in ON condition. The reactive power supplied by the capacitors adds on to the transmission lines due to the absence of inductance.

## Slide 34
As a result voltage at the receiving end or consumer end increases and is more than the voltage at the supply end. This is known as Ferranti effect.
The Ferranti Effect occurs when current drawn by the distributed capacitance of the transmission line itself is greater than the current associated with the load at the receiving end of the line.
Therefore, the Ferranti effect tends to be a bigger problem on lightly loaded lines, and especially on underground cable circuits where the shunt capacitance is greater than with a corresponding overhead line.

## Slide 35
This effect is due to the voltage drop across the line inductance (due to charging current) being in phase with the sending end voltages.
As this voltage drop affects the sending end voltage, the receiving end voltage becomes greater. The Ferranti Effect will be more pronounced the longer the line and the higher the voltage applied.
The Ferranti Effect is not a problem with lines that are loaded because line capacitive effect is constant independent of load, while inductance will vary with load.
As inductive load is added, the VAR generated by the line capacitance is consumed by the load.

## Slide 36: How to Reduce Ferranti Effect:
Shunt Reactors and Series Capacitors
The need for large shunt reactors appeared when long power transmission lines for system voltage 220 kV & higher were built.
The characteristic parameters of a line are the series resistance, inductance (due to the magnetic field around the conductors) & the shunt capacitance (due to the electrostatic field to earth).
When the line is loaded, there is a voltage drop along the line due to the series inductance and the series resistance. When the line is energized but not loaded or only loaded with a small current, there is a voltage rise along the line (the Ferranti-effect).

## Slide 37
To stabilize the line voltage the line inductance can be compensated by means of series capacitors and the line capacitance to earth by shunt reactors. Series capacitors are placed at different places along the line while shunt reactors are often installed in the stations at the ends of line.
Shunt reactors contain the same components as power transformers. The main difference is the reactor core limbs, which have non-magnetic gaps inserted between packets of core steel.

## Slide 38: Voltage control techniques in power systems
Control of voltage levels is accomplished by controlling the production, absorption, and flow of reactive power at all levels in the power system.
Generating units provide the basic means of voltage control.
Additional means are usually required to control voltage throughout the system:
  sources or sinks of reactive power, such as shunt capacitors, shunt reactors, synchronous condensers, and static var compensators (SVCs)
  line reactance compensators, such as series capacitors
  regulating transformers, such as tap-changing transformers and boosters

## Slide 39
Shunt capacitors and reactors, and series capacitors provide passive compensation
  are either permanently connected to the transmission and distribution system, or switched
  contribute to voltage control by modifying the network characteristics
Synchronous condensers and SVCs provide active compensation; the reactive power absorbed/ supplied by them are automatically adjusted so as to maintain voltages of the buses to which they are connected.
  together with the generating units, they establish voltages at specific points in the system
  voltages at other locations in the system are determined by active and reactive power flows through various circuit elements, including the passive compensating devices

## Slide 40: Shunt Reactors
Used to compensate the undesirable voltage effects associated with line capacitance
  limit voltage rise on open circuit or light load
  increases effective ZC
  reduces the effective natural load , i.e., voltage at which flat voltage profile is achieved
They are connected either:
  directly to the lines at the ends, or
  to transformer tertiary windings; conveniently switched as var requirements vary
Line reactors assist in limiting switching surges
In very long lines, at least some reactors are required to be connected to lines

## Slide 41: Shunt Capacitors
Used in transmission systems to compensate for I 2X losses
Connected either directly to H.V. bus or to tertiary winding of transformers
Normally distributed throughout the system so as to minimize losses and voltage drops
Usually switched: a convenient means of controlling voltage
Advantages: low cost and flexibility of installation and operating
Disadvantages: Q output is proportional to square of the voltage; hence Q output reduced at low voltages
Shunt capacitors are used extensively in distribution systems for power factor correction and feeder voltage control

## Slide 42: Series Capacitors
Connected in series with the line
Used to reduce effective inductive reactance of line
  increases maximum power
  reduces I 2X loss
Series capacitive compensation in effect reduces both:
  characteristic impedance ZC, and
  electrical length θ
Typical applications
  improve power transfer compatibility
  alter load division among parallel lines
  voltage regulation

## Slide 43: Synchronous Condenser
A synchronous machine running without a prime mover or a mechanical load.
Depending on field excitation, it can either absorb or generate vars
With a voltage regulator, it can automatically adjust vars to maintain constant voltage
Started as an induction motor and then synchronized
Normally connected to tertiary windings of transformers
Unlike a SVC, a synchronous condenser has an internal voltage
Speed of response not as fast as that of an SVC

## Slide 44: Static VAR Compensators (SVC)
Shunt connected static var generators and/or absorbers whose outputs are varied so as to control specific power system quantities.
The term static is used to denote that there are no moving or rotating components
Basic types of SVCs:
  thyristor-controlled reactor
  thyristor-switched capacitor
  saturated reactor
A static var system (SVS) is an aggregation of SVCs and mechanically switched capacitors or reactors whose outputs are coordinated.
When operating at its capacitive limit, an SVC behaves like a simple capacitor

## Slide 45: Tap-Changing Transformers
Transformer with tap-changing facilities constitute an important means of controlling voltages throughout the power system
Control of a single transformer will cause changes in voltages at its terminals
  in turn this influences reactive power flow
  resulting effect on the voltages at other buses will depend on network configuration and load/generation distribution
Coordinated control of the tap changers of all transformers interconnecting the subsystems required to achieve overall desired effect
During high system load conditions, network voltages are kept at highest practical level to
  minimize reactive power requirements
  increase effectiveness of shunt capacitors and line charging

## Slide 46
The highest allowable operating voltage of the transmission network is governed by
  requirement that insulation levels of equipment not be exceeded
  need to take into consideration possible switching operations and outage conditions
During light load conditions, it is usually required to lower network voltages
  reduce line charging
  avoid underexcited operation of generators
Transformers with under-load tap-changers (ULTC) are used to take care of daily, hourly, and minute-by-minute variations in system conditions
Off-load tap-changing transformers used to take care of long-term variations due to system expansion, load growth, or seasonal changes